SECTION 13 34 13 – STRUCTURAL SWIMMING POOL ENCLOSURE SPECIFICATION

Revise this section by deleting and inserting text to meet project-specific requirements.

Specifier: Consult Structures Unlimited, Inc. for assistance at info@structutresunlimitedinc.com or 1-800-225-3895.

Some specification choices are very involved and require consultation in order for the project’s performance to be as desired by the Owner and Architect.

- GENERAL

      - SUMMARY

        - All requirements of the contract documents form an integral part of the work specified herein; in particular, refer to the conditions (general or otherwise) and Division 1 of the specifications, including all subdivisions thereof.

        - This specification covers the design, manufacturing and installation of a prefabricated enclosure, to be fabricated with a tubular aluminum structural framing system and a thermally broken translucent roof panel system.  Field fabricated systems shall not be allowed.

        - Requests for substitutions must be approved by addendum no later than ten days prior to bid due dates and in keeping with Division 1 (Substitutions) of the specifications.

        - Should the Contractor propose to make any changes or substitutions to the specification and drawings, such changes or substitutions shall be made only upon approval of the Owner.  All changes proposed by the Contractor and approved by the Owner shall be made at no additional cost to the Owner.  If substitutions require design or other engineering / architectural services, the services shall be provided by the architect.  The cost of engineering / architectural services for substitutions shall be at the expense of the Contractor.

        - Work included: Supply all material and labor required to deliver and install the structural enclosure system. The following major items included are:

          - Structural aluminum box beam superstructure

          - Thermally broken insulated translucent sandwich panels

          - Aluminum installation system

          - Aluminum/flexible flashing

          - (Optional) Electrically powered operable roof system

        - Related Sections:

- Insert sections in subparagraph below that contain requirements the Contractor might expect to find is this section but are specified in other sections.

          - <Insert Related Sections>

      - SUBMITTALS

        - Submit manufacturer’s product data. Include construction details, material descriptions, profiles and finishes of components.

        - Submit shop drawings.  Include plans, elevations and details.

        - Submit manufacturer’s color charts showing the full range of colors available for factory finished aluminum.

          - When requested, submit samples for each exposed finish required, in same thickness and material indicated for the work and in size indicated below. If finishes involve normal color variations, include sample sets consisting of two or more units showing the full range of variations expected.

- Select sandwich panel sample size required.

            - Sandwich panels:  [7” x 12”] [14”x28”] units

            - Factory finished aluminum:  5” long sections

        - Product reports to be furnished by enclosure system manufacturer in accordance with Division 1, Submittals. Submit product reports from a qualified independent testing agency indicating each type of panel system that complies with the project performance requirements, based on comprehensive testing of current products. Previously completed reports will be acceptable if for current manufacturer and indicative of products used on this project.

Delete product reports below that are not applicable.

          - Reports required (if applicable) are:

            - International Building Code Evaluation Report (AC 177)

            - Flame Spread and Smoke Developed (UL 723)  – Submit UL Card

            - Burn Extent (ASTM D 635)

            - Color Difference (ASTM D 2244)

            - Impact Strength (UL 972)

            - Bond Tensile Strength (ASTM C 297 after aging by ASTM D 1037)

            - Bond Shear Strength (ASTM D 1002)

            - Beam Bending Strength (ASTM E 72)

            - Insulation U-Factor (NFRC 100)

            - Solar Heat Gain Coefficient (NFRC or Calculations)

            - Condensation Resistance Factor (AAMA 1503) (Thermally Broken only)

            - 1200°F Fire Resistance (SWRI)

            - Fall Through Resistance (ASTM E 661)

            - Class A Roof Covering Burning Brand (ASTM E 108)

            - UL Listed Class A Roof System (UL 790) (Optional) – Submit UL Card

        - Submit current documentation indicating regular, independent quality control monitoring under a nationally recognized building code review and listing program.

- Please consult with Structures Unlimited, Inc. for Daylighting report to be generated for accurate figures to insert.

        - (Optional) Provide Daylight Autonomy Report showing that the proposed translucent daylighting system will provide <Insert Number> lux in the daylit areas for an average of <Insert Number> % of the daylight hours for the entire year.

      - CLOSEOUT SUBMITTALS

        - Provide project maintenance manuals.

      - QUALITY ASSURANCE

        - Manufacturer’s Qualifications:

          - Material and products shall be manufactured by a company continuously and regularly employed in the manufacture of specified materials for a period of at least ten consecutive years and which can show evidence of those materials being satisfactorily used on at least six projects of similar size, scope and location. At least three of the projects shall have been in successful use for ten years or longer.

          - Panel system must be listed by an ANSI accredited Evaluation Service, which requires quality control inspections and fire, structural and water infiltration testing of sandwich panel systems by an accredited agency.

          - Quality control inspections shall be conducted at least once each year and shall include manufacturing facilities, sandwich panel components and production sandwich panels for conformance with AC177 “Translucent Fiberglass Reinforced Plastic (FRP) Faced Panel Wall, Roof and Skylight Systems” as issued by the ICC-ES.

        - Installers Qualifications: Installation shall be by the manufacturer or an experienced installer, which has been in the business of installing specified enclosure systems for at least ten years and can show evidence of satisfactory completion of projects of similar size, scope and type.

      - PERFORMANCE REQUIREMENTS

        - The manufacturer shall be responsible for the configuration and fabrication of the structural aluminum system and the thermally broken structural translucent roof system with specified thermal properties.

          - When requested, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

          - Structural Loads:  Provide enclosure system capable of handling the following loads:

- Insert structural loads, as determined by project’s structural engineer in subparagraphs below.  Insert all loads in PSF, not wind speed.  If drift load is applicable to the project, provide the necessary profile.

            - Roof Live Load, on horizontal projected surface, minimum: <Insert Number> PSF

            - Roof Snow Load, on horizontal projected surface, minimum: <Insert Number> PSF

            - Roof Snow Drift Load, on horizontal projected surface, minimum: <Insert Number> PSF, <Provide Profile>

            - Base Wind Load <Insert Number> PSF factored per applicable Building Code

      - DESIGN

        - Description: Enclosure System

- Retain subparagraphs below if information noted below is available. Remove subparagraphs below if information has not yet been finalized. If information is not known, it is best to remove subparagraphs to avoid possible conflicts with the final contract documents.

          - Nominal Size: <Insert Span> x <Insert Length>

          - Aluminum Box Beam Size: [4”x8”] [5”x10”] [6”x13”] [6 3/8”x 16”] [6 3/8”x18”]

          - Eave Height: <Insert Height>

          - Roof Pitch: <Insert Angle>

      - DELIVERY, STORAGE AND HANDLING

        - Deliver enclosure system, components and materials in manufacturer’s standard protective packaging.

        - Store enclosure system panels on the long edge; several inches above the ground, blocked and under cover to prevent warping in accordance with manufacturer’s storage and handling instructions.

      - WARRANTY

        - Provide manufacturer's and installer's written warranty agreeing to repair or replace enclosure system work, which fails in materials or workmanship within one year from the date of delivery. Failure of materials or workmanship shall include leakage, excessive deflection, deterioration of finish on metal in excess of normal weathering, defects the insulated translucent sandwich panels and other components of the work.

- PRODUCTS

      - MANUFACTURER

        - The basis for this specification is for products manufactured by Structures Unlimited, Inc. Other manufacturers may bid this project provided they comply with all of the performance requirements of this specification and submit evidence thereof.  Listing other manufacturers’ names in this specification does not constitute approval of their products or relieve them of compliance with all the performance requirements contained herein.

        - Structures Unlimited, Inc., Tel: (800) 225-3895 – Email: info@structuresunlimitedinc.com

      - PANEL COMPONENTS

        - Translucent roof system shall be compatible with the aluminum structural system.

        - Structural roof panels shall have an overlap leading edge of 1 5/8 inches to provide a water shedding weather tight seal at horizontal lap-joint panel connections. Overlap system shall not cause damming of water.

        - Structural roof panels shall expand and contract at the same ratio as the aluminum structural system (1.24x10-5.in/in/degree F).

      - FACE SHEETS

        - Translucent faces: Manufactured from glass fiber reinforced thermoset resins, formulated specifically for architectural use.

          - Thermoplastic (e.g. polycarbonate, acrylic) faces are not acceptable.

          - Face sheets shall not deform, deflect, or drip when subjected to fire or flame.

        - Interior Face Sheets

Specify 25 which meets IBC Class A which may be required in unsprinklered, occupied spaces or exit ways – see interior finish table in IBC Chapter 8.

Specify 50 for the standard panel, which meets IBC Class B Interior Finish requirements for most building spaces.

          - Flame spread: Underwriters Laboratories (UL) listed, which requires periodic unannounced retesting, with flame spread rating no greater than [50] [25] and smoke developed no greater than 250 when tested in accordance with UL 723.

          - Burn extent by ASTM D 635 shall be no greater than 1”.

        - Exterior Face Sheets

Color stability – For standard exterior face: select 5 years exposure.

If for UL Listed Class A Roof Class A sheet face required: select 3 years.

          - Color stability: Full thickness of the exterior face sheet shall not change color more than 3 CIE Units DELTA E by ASTM D 2244 after [3] [5] years outdoor South Florida weathering at 5° facing south, determined by the average of at least three white samples with and without a protective film or coating to ensure long-term color stability. Color stability shall be unaffected by abrasion or scratching.

For paragraph a, the impact strength of the standard .070” thick SW exterior face sheet is 70 ft. lbs.       The optional Hi-Impact face sheet is 230 ft. lbs. which may be required in vandal prone exposures among others.

            - Strength: Exterior face sheet shall be uniform in strength, impenetrable by hand held pencil and repel an impact minimum of [70 ft. lbs.] [230 ft. lbs.] without fracture or tear when impacted by a 3-1/4” diameter, 5 lb. free-falling ball per UL 972.

            - Erosion Protection: Integral, embedded-glass erosion barrier.

        - Appearance:

CAUTION: Face sheet colors affect solar properties. Refer to Light Transmission/SGHC chart.

Exterior face sheets:  Enter thickness and color.

Standard exterior face sheet is .070” thick and is available in standard White or Crystal.

Optional Kal-tints are available in Greenish-Blue, Aqua, Rose and Ice-Blue.

Optional Hi-Impact is .052” thick in White only.

UL Class A roof – Enter .070” thick and is available in standard White Type A or Crystal Type A

Interior face sheet: Enter thickness and color.

Standard interior face sheet, either flame spread, is .045” thick and is available in White or Crystal.

Optional Hi-Impact is .052” thick in White only.

            - Exterior face sheet: Smooth, <Insert Thickness> thick and <Insert Color> in color.

            - Interior face sheet:  Smooth, <Insert Thickness> thick and <Insert Color> in color.

            - Face sheets shall not vary more than ± 10% in thickness and be uniform in color.

        - Grid Core:

          - Thermally broken composite I-beam grid core shall be of 6063-T6 or 6005-T5 alloy and temper with provisions for mechanical interlocking of muntin-mullion and perimeter. Width of I-beam shall be no less than 7/16”.

          - I-beam thermal break:  Minimum 1”, thermoset fiberglass composite.

        - Laminate Adhesive:

          - Heat and pressure resin type adhesive engineered for structural sandwich panel use, with minimum 25-years field use. Adhesive shall pass testing requirements specified by the International Code Council “Acceptance Criteria for Sandwich Panel Adhesives".

          - Minimum tensile strength of 750 PSI when the panel assembly is tested by ASTM C 297 after two exposures to six cycles each of the aging conditions prescribed by ASTM D 1037.

          - Minimum shear strength of the panel adhesive by ASTM D 1002 after exposure to four separate conditions:

            - 50% Relative Humidity at 68° F: 540 PSI

            - 182° F: 100 PSI

            - Accelerated Aging by ASTM D 1037 at room temperature: 800 PSI

            - Accelerated Aging by ASTM D 1037 at 182° F: 250 PSI

      - PANEL CONSTRUCTION

        - Provide sandwich panels of flat fiberglass reinforced translucent face sheets laminated to a grid core of mechanically interlocking I-beams.  The adhesive bonding line shall be straight, cover the entire width of the I-beam and have a neat, sharp edge.

1. Select 2 ¾” or 4” panels.

2-4. Light Transmission, Solar Heat Gain Coefficient and Panel U-factor are closely linked and must be specified accordingly. Refer to Light Transmission/SHGC Chart.

Furthermore, light transmission needs to be carefully chosen to meet the daylighting expectations of the owner to avoid too much light with resulting unwanted glare and solar heat or too little light to be useful. See www.DaylightModeling.com, which should be performed and agreed upon prior to final design and specification.

5. Insert Grid nominal size (as viewed) and pattern. Standard grids 12 x 24 shoji, 8 x 20 shoji, or 12” x 12” square pattern called Tuckerman. Custom sizes and patterns available.

          - Thickness: [2-3/4”] [4”]

          - Light transmission: <Insert Value> %

          - Solar heat gain coefficient: <Insert Value>

          - Panel U-factor by NFRC certified laboratory: <Insert U-factor>

          - Grid pattern: Nominal size <Insert Grid Size>; pattern  <Insert Pattern>

        - Standard panels shall deflect no more than 1.9” at 30 PSF in 10’-0” span without a supporting frame by ASTM E 72.

        - Standard panels shall withstand 1200° F fire for minimum one hour without collapse or exterior flaming.

        - Thermally broken panels: Minimum Condensation Resistance Factor of 80 by AAMA 1503 measured on the bond line.

Delete paragraphs E, F and G if not applicable. Consult IBC or local Code authority for requirements.

Standard enclosure panels pass Class A Burning Brand.

UL790 Class A Built Up Roof construction is available as an option. Delete F if not required.

        - Enclosure roof panels shall pass Class A Roof Burning Brand Test by ASTM E 108.

        - (Optional) Enclosure roof panels shall be UL listed as a Class A Roof by UL 790, which requires periodic unannounced factory inspections and retesting by Underwriters Laboratories.

        - Roof System shall meet the fall through requirements of OSHA 1910.23 as demonstrated by testing in accordance with ASTM E 661, thereby not requiring supplemental screens or railings.

      - BATTENS AND PERIMETER CLOSURE SYSTEM

        - Closure system: Extruded aluminum 6063-T6 and 6063-T5 alloy and temper clamp-tite screw type closure system.

        - Sealing tape: Manufacturer’s standard, pre-applied to closure system at the factory under controlled conditions.

        - Fasteners: Various series stainless steel screws for aluminum closures, excluding final fasteners to the building.

- Insert a color from manufacturer’s standards. Consult with Structures Unlimited, Inc.

        - Finish: Manufacturer's factory applied finish, which meets the performance requirements of AAMA 2604.  Color to be <Insert Color and Number> [selected from manufacturer's standards].

      - SUPERSTRUCTURE

- Select design required for the application – “rigid frame” or “truss”.  Consult with Structures Unlimited, Inc. to ensure correct design is selected.

        - The superstructure shall be pre-fabricated of extruded aluminum alloy 6005-T5, 6005A-T61 or 6061-T6 box beams.  Ferrous metals shall not be allowed.  All structural components, gusset plates and fasteners shall be aluminum.  All parts shall be pre-assembled at the factory and knocked down for shipment.  System shall be a <Insert Design> [Rigid Frame] [Truss] design.

- Insert a color from manufacturer’s standards. Consult with Structures Unlimited, Inc.

        - Finish: Manufacturer's factory applied finish, which meets the performance requirements of AAMA 2604.  Color to be <Insert Color and Number> [selected from manufacturer's standards].

        - Aluminum structural system design and calculations must be furnished in accordance with the Aluminum Association “Specifications for Aluminum Structures” and the applicable building code.  Design calculations must be prepared and stamped by a licensed Professional Engineer.

        - All structural frame assemblies shall have internal gusset connections at the ridge and knee connections.  Fastening of components will be with aluminum drive rivets, screw/bolts and galvanized bolts.  Steel bolts, nuts and washers shall not be permitted.

        - Wind bracing will be located and sized as dictated by the structural design.  Tubular wind bracing sections shall be used to reduce the flex that can occur in strap and angle bracing.

      - MOTORIZED ROOF

        - Operable sections are 2 ¾” thick fiberglass reinforced translucent face sheets laminated to a grid core of mechanically interlocking I-beams.  Screen units are provided to cover the open area.

        - Operation: Roof panels to slide down by gravity and pull up under power by use of a 1 horsepower, single phase 60 cycles, 208 volts totally enclosed gear motor and stainless steel aircraft cable systems.

      - SLIDING GLASS DOORS

        - Sliding glass doors are 8’-0” x 6’-8” with 5/8” tempered insulated clear glass. Main frame and panel members shall be constructed of extruded aluminum alloy 6063-T5 with a thermal break separating the exterior and interior portions of the frame.

        - Sliding glass doors are equipped with an interior latch and interior and exterior door pulls.

      - EGRESS DOOR

        - Kawneer 350 medium stile and rail door with full glass. Door to be complete with 1 ½ pair hinges (US26D) Dor-o-matic concealed vertical rod exit device with an exterior pull handle, concealed overhead closer, standard weatherstrip and threshold.

      - SIDEWALL AND GABLE INFILL MATERIAL

        - Fixed Glass: All glass shall be insulated tempered 5/8” clear. (1” Optional).

        - Translucent insulated wall panels with insulation value and interior and exterior face sheets similar to the roof panels.

- EXECUTION

      - EXAMINATION

        - Installer shall examine substrates, supporting structure and installation conditions.

        - Do not proceed with structural enclosure installation until unsatisfactory conditions have been corrected by the general contractor.

      - PREPARATION

        - Metal Protection:

          - Where aluminum will contact dissimilar metals, protect against galvanic action by painting contact surfaces with primer or by applying sealant or tape recommended by manufacturer for this purpose.

          - Where aluminum will contact concrete, masonry or pressure treated wood, protect against corrosion by painting contact surfaces with bituminous paint or method recommended by manufacturer.

        - The general contractor shall install foundations, curbs, footings and/or lintels designed to withstand the thrust generated by the enclosure.

        - Anchor Bolts shall be supplied and installed by the general contractor.  Enclosure anchoring system will be as per manufacturer’s standards.

        - The general contractor shall provide temporary enclosures if required.

      - INSTALLATION

        - The manufacturer or authorized installer shall install the enclosure system in strict accordance with the approved shop drawings.  Fastening and sealing shall be in strict accordance with manufacturer’s approved shop drawings.  All aluminum shall be cleaned before sealant are applied.

        - No finish work, such as painting, plastering or interior trim items to be supplied or installed by the manufacturer.

        - After other trades have completed work on adjacent material, carefully inspect translucent panel installation and make adjustments necessary to ensure proper installation and weather tight conditions.

END OF SECTION 13 34 13