Section 08 3493

AUTOMATIC overhead coiling fabric Fire Curtain

# General

## Summary

### Section Includes:

#### Fusible link activated, overhead coiling fabric fire curtain.

#### Self-closing without auxiliary power.

#### For window openings up to eight feet wide by 8 feet high.

### Related Requirements:

#### 09 2200 Load bearing header framing

#### 09 9100Paint: Field painting of specified components.

## References

### ASTM Codes and Standards:

#### ASTM - E84 - Test Method for Surface Burning Characteristics of Building Materials

### UL Standards:

#### 10B – Fire test for door assemblies.

#### 10C – Fire test for door assemblies with positive pressure

#### 10D – Fire test for fire resistant curtains.

## submittals

### Comply with Section 01 3300Submittal Procedures:

#### Product data.

#### Shop drawings:

##### Include opening dimensions.

##### Show and identify related work performed under other sections of the specifications.

#### Quality Assurance/Control Submittals:

##### Certifications.

##### Manufacturer’s installation instructions and testing procedures.

## closeout submittals

### Comply with Section 01 7700Project Closeout:

#### Operation and maintenance manual.

#### Manufacturer’s warranty.

## Quality Assurance

### Certifications:

#### ETL Listing to UL standards:

##### 10B - Fire test for fire doors: 20-minutes

##### 10C – Fire test for fire doors: 20-minutes.

##### 10D – Fire test for fire resistant curtains: 2-hours.

### Pre-Installation Meeting:

#### Schedule and convene a pre-installation meeting prior to commencement of field operations with representatives of the following in attendance: Owner, Architect, General Contractor, fire curtain sub-contractor.

#### Review substrate conditions, requirements of related work, installation instructions, storage and handling procedures, and protection measures.

#### Document responsibilities of various parties and deviations from specifications and installation instructions.

## Delivery, Storage, and Handling

### Comply with Section 01 6600Delivery, Storage, and Handling.

### Comply with manufacturer’s instructions.

## Warranty

### Provide manufacturer’s standard one year warranty.

### Maintenance and Testing:

#### Perform minimum semi-annual maintenance and testing on each fire curtain as required by the manufacturer’s warranty, code agency evaluation reports, and as required by local authority having jurisdiction.

#### Provide test documentation.

# Products

## ManufactureD units

### Model M1000.

### Manufacturer:

#### Smoke Guard, Inc.

#### Distributed by Smoke Guard, 287 N. Maple Grove, Boise, Idaho  83704 www.smokeguard.com/

### Label each fire curtain with following information:

#### Manufacturer’s name.

#### Label of quality control agency.

## Performance / DESIGN CRITERIA

### Test normal and fire operation: Curtain to deploy on activation of fusible link contained within the system. Curtain shall descend by gravity and retract by manual operation.

#### Raise curtain after test and reset fusible link.

#### Reset curtain after test or operation of unit using manual crank. No service call needed. No replacement parts needed.

### Test to 1,000 cycles.

## Components

### Curtain Fabric:  SG Tex 32 - Glass fiber material coated on one side with a polyester polyurethane latex and steel wire reinforcement.

#### Rating:  120 minutes.

### Side Guide Assembly:

#### See manufacturer’s standard side guide.

### Housing/Bearing Type:  Standard or support bearing.

### Bottom Bar: Weighted for self-closing by gravity.

### Finishes:

#### Manufacturer’s standard galvanized finish.  Optional finishes available at extra cost including: field painting, stainless steel or powder coat.

## fabrication

### Installation Configuration:  Housing attached directly to wall.

### Fabricate and install mounting brackets, hardware, and fasteners needed to attach fire curtain assembly to building structure.

# Execution

## Examination

### Examine substrates upon which work will be installed.

#### Verify related work performed under other sections is complete and in accordance with shop drawings.

#### Verify wall surfaces are acceptable for installation of fire curtain system components.

### Coordinate with responsible entity to perform corrective work on unsatisfactory substrates.

### Commencement of work by installer is acceptance of substrate.

## INSTALLATION

### Install fire curtain system components in accordance with manufacturer’s installation instructions.

## Field Quality Control

### Field Test: Follow manufacturer’s cycle test procedures.

#### Notify Owner’s Representative, local Fire Marshal minimum one week in advance of scheduled testing.

#### Complete maintenance service record.

## Demonstration

### Demonstrate required testing and maintenance procedures to Owner’s Representative.

End of Section